## Sheet1
Huawei R4875G1 Rectifier Module | Edited by mjpalmowski
Baud Rate 125kbps
Extended Frame
Command/Response | Addr |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  |  | ID |  |  |  | Value
Request Data Frames: | 0x108040FE ** |  | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | Value Divisor
Receive Data: | 0x1081407F *** |  | 0x01 | 0x0E | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x0A |  | Unknown frame
|  |  | 0x01 | 0x70 | 0x00 | 0x00 | Input Power |  |  |  | /1024
|  |  | 0x01 | 0x71 | 0x00 | 0x00 | Input Frequency |  |  |  | /1024
|  |  | 0x01 | 0x72 | 0x00 | 0x00 | Input Current |  |  |  | /1024
|  |  | 0x01 | 0x73 | 0x00 | 0x00 | Output Power |  |  |  | /1024
|  |  | 0x01 | 0x74 | 0x00 | 0x00 | Efficiency |  |  |  | /1024
|  |  | 0x01 | 0x75 | 0x00 | 0x00 | Output Voltage |  |  |  | /1024
|  |  | 0x01 | 0x76 | 0x00 | 0x00 | Output Current Max |  |  |  | /15 | /15 if Pin 9 and Pin 10 are connected (to release 75A max current)
|  |  | 0x01 | 0x78 | 0x00 | 0x00 | Input Voltage |  |  |  | /1024
|  |  | 0x01 | 0x7F | 0x00 | 0x00 | Output Temperature |  |  |  | /1024
|  |  | 0x01 | 0x81 | 0x00 | 0x00 | Output Current |  |  |  | /1024 | This output current appears more accurate (on my single unit/sample)
|  |  | 0x01 | 0x82 | 0x00 | 0x00 | Output Current |  |  |  | /1024 | Not sure what this is?
|  |  | 0x01 | 0x83 | 0x00 | 0x10 | Unknown- normally zero
|  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  |  | 0: ID; 4: Value | Value Multiplier
Set Data: | 0x108180FE* |  | 0x01 | 0x00 | 0x00 | 0x00 | On-line Output Voltage |  |  |  | V * 102 | Acceptable range 41.5 to 58.5V in 0.1V steps. Example: 460 (46.0V) * 102 = 00 00 B7 48
|  |  | 0x01 | 0x01 | 0x00 | 0x00 | Off-line/Default Output Voltage |  |  |  | V * 102 | Acceptable range 48 to 58.5V in 0.1V steps
|  |  | 0x01 | 0x02 | 0x00 | 0x00 | Overvoltage Protection? (Untested) |  |  |  | V * 102 | Acceptable range 56.5 to 60.5V (as per datasheet)
|  |  | 0x01 | 0x03 | 0x00 | 0x00 | On-line Current Limit |  |  |  | A * 1.5 | Acceptable range 0 to 90.5A in 0.1A steps. Example: 500 (50.0 A) * 1.38 = 00 00 02 B2 | *1.5 if in full power mode
|  |  | 0x01 | 0x04 | 0x00 | 0x00 | Off-line/Default Output Current Limit |  |  |  | A * 1.5 | Acceptable range 0 to 90.5A in 0.1A steps | *1.5 if in full power mode
|  |  | 0x01 | 0x07 | 0x00 | 0x00 | Current limit?? |  |  |  | A * 1.157 | Not tested…
|  |  | 0x01 | 0x32 | 0x00 | 0xXX | 0x00 | 0x00 | 0x00 | 0x00 | - | XX: 01 - disable Huawei (standby mode), 00 - enable Huawei
|  |  | 0x01 | 0x34 | 0x00 | 0xXX | 0x00 | 0x00 | 0x00 | 0x00 |  | XX: 01 -Turn on the fans at full power, 00 - automatic fan speed control (On-line)
|  |  | 0x01 | 0x35 | 0x00 | 0xXX | 0x00 | 0x00 | 0x00 | 0x00 |  | XX: 01 -Turn on the fans at full power, 00 - automatic fan speed control (Off-line)
Value Multiplier
| 0x1001117e **** |  | 0x00 | 0x01 | 0x00 | 0x01 | 0x00 | 0x00 | 0x00 | 0x00 |  | Byte 3 is Output Enabled Byte, It is 1 when the unit is hibernating and 0 when it is ON
|  |  | 0x00 | 0x01 | 0x00 | 0x00 | Output Current |  |  |  | /15 | This is an unsolicited message reporting the DC current, encoded in the last four bytes
The rectifier can operate in two states:
Off-line is when there is no CAN communication (i.e. standalone operation). This occurs on power-up or if CAN communication has timed-out (Orange LED slowly blinking).
On-line values are only valid when CAN communication is present (Orange LED not blinking). These values are volatile and reset to default on loss of CAN comms.
CAN communication time-out is approximately 60 seconds. i.e. if you stop sending valid CAN messages to the rectifier, the rectifier will switch to Off-line/Default values in approximately 60 seconds.
*0x108180FE for first Huawei, 0x108280FE for second Huawei, etc. 0x108080FE for all units in the system
** 0x108040FE to request status messages from all recitfiers, when more than one Rectifier is on the CAN BUS you can use 0x108140FE to request status from rectifier 1; 0x108240FE to request from No.2 rectifier etc
***0x1081407F is the ID that reports for the first rectifier (true also when only one is on the BUS); 0x1082407F is the ID for status messages from No.2 rectifier etc.
****0x1001117e for multible unit the message ID is following the same logic 0x1001117e 0x1002117 e0x1003117e etc…
Fan-speed control:
Request Data Frames: | 0x108182FE |  | 0x01 | 0x87 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00
|  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  |  | 0: ID; 4: Value | Value Multiplier
Receive Data: | 0x1081827F |  | 0x01 | 0x87 | auto FAN duty |  | SET min FAN duty |  | RPM |  | /256
Value Multiplier
Set Data: | 0x108080FE |  | 0x01 | 0x14 | Percent Duty Cycle |  | 0x00 | 0x00 | 0x00 | 0x00 | *256
Set AC Current Limit:
Value Multiplier
Set Data: | 0x108080FE |  | 0x01 | 0x09 | 0x00 | 0 disable 1 enable limit | 0x00 | 0x00 | Input Current Limit |  | *1024
alternative parameter request/response
CAN ID | Value ID | Value | 0: Description
request:
0x108182FE | 0x00080000 | 00000000
0x108182FE | 0x01700000 | 00000000
0x108182FE | 0x01710000 | 00000000
0x108182FE | 0x01720000 | 00000000
0x108182FE | 0x01730000 | 00000000
0x108182FE | 0x01740000 | 00000000
0x108182FE | 0x01750000 | 00000000
0x108182FE | 0x01760000 | 00000000
0x108182FE | 0x01770000 | 00000000
0x108182FE | 0x01780000 | 00000000
0x108182FE | 0x017c0000 | 00000000
0x108182FE | 0x017e0000 | 00000000
0x108182FE | 0x017f0000 | 00000000
0x108182FE | 0x01800000 | 00000000
0x108182FE | 0x01810000 | 00000000
0x108182FE | 0x01820000 | 00000000
0x108182FE | 0x01830000 | 00000000
0x108182FE | 0x01840000 | 00000000
0x108182FE | 0x01850000 | 00000000
0x108182FE | 0x01860000 | 00000000
0x108182FE | 0x01870000 | 00000000
response:
0x1081827e | 0x00080000 | 0x01010103 | 0: undocumented
0x1081827e | 0x01700000 | 0x00000000 | 0: AC input power sf /1024 (0x70)
0x1081827e | 0x01710000 | 0x0000c7eb | 0: Grid Frequency sf /1024 (0x71)
0x1081827e | 0x01720000 | 0x00000000 | 0: AC input current sf /1024 (0x72)
0x1081827e | 0x01730000 | 0x00000000 | 0: DC output power sf /1024 (0x73)
0x1081827e | 0x01740000 | 0x00000000 | 0: efficiency sf /1024 (0x74)
0x1081827e | 0x01750000 | 0x00000570 | 0: output voltage 1.36V sf /1024 (0x75)
0x1081827e | 0x01760000 | 0x00000091 | 0: output live current limit sf /20 7.25A (0x76)
0x1081827e | 0x01770000 | 0x00000075 | 0: %power available sf /1024 11.42% here, usually 100%
0x1081827e | 0x01780000 | 0x00039400 | 0: Line Voltage sf /1024 (0x78)
0x1081827e | 0x017c0000 | 0x0004cec0 | 0: internal DC-BUS Voltage sf /1024
0x1081827e | 0x017e0000 | 0x00006800 | 0: PFC (?Power Factor Correction) module temperature 26C sf /1024
0x1081827e | 0x017f0000 | 0x00004c00 | 0: input temperature 19C sf /1024 (0x80)
0x1081827e | 0x01800000 | 0x00006800 | 0: output temperature 26C sf /1024 (0x7F)
0x1081827e | 0x01810000 | 0x00000000 | 0: output current sf /1024 (0x81)
0x1081827e | 0x01820000 | 0x00000000 | 0: output current2 sf /1024 (0x82)
0x1081827e | 0x01830001 | 0x00000204 | 0: undocumented (status/error codes)
0x1081827e | 0x01840000 | 0x00000570 | 0: undocumented
0x1081827e | 0x01850000 | 0x000005ee | 0: undocumented
0x1081827e | 0x0186000b | 0x00000000 | 0: undocumented
0x1081827e | 0x01870000 | 0x00000000 | 0: Fan Speed sf /256
How to use:
To receive each of these messages send to ID 0x108182FE the relevant value ID followed by all zeros.
for example send to ID 0x108182FE this message: 0x0171000000000000
the rectifier replies with ID 0x1081827E with a message containing the same value ID and the value of the grid frequency in the last four bytes.
for example: 0x017100000000c7eb c7eb-HEX is 51179 divide by 1024 to get the final value of 49.98 HZ
To receive a reply from the second device send to ID 0x108282FE this message 0x0171000000000000
the second rectifier replies with ID 0x1082827E
why would you use this and not the known bulk request for all values?
If you need high frequency updates for some values to get tight regulation, you can request them one by one rather than spamming the bus with all values.