## Sheet1
Huawei R4875G1 Rectifier Module | Edited by mjpalmowski
Baud Rate 125kbps
Extended Frame
Command/Response | Addr | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | ID |  |  |  | Value
Request Data Frames: | 0x108040FE ** | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | Value Divisor
Receive Data: | 0x1081407F *** | 0x01 | 0x0E | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x0A |  | Unknown frame
|  | 0x01 | 0x70 | 0x00 | 0x00 | Input Power |  |  |  | /1024
|  | 0x01 | 0x71 | 0x00 | 0x00 | Input Frequency |  |  |  | /1024
|  | 0x01 | 0x72 | 0x00 | 0x00 | Input Current |  |  |  | /1024
|  | 0x01 | 0x73 | 0x00 | 0x00 | Output Power |  |  |  | /1024
|  | 0x01 | 0x74 | 0x00 | 0x00 | Efficiency |  |  |  | /1024
|  | 0x01 | 0x75 | 0x00 | 0x00 | Output Voltage |  |  |  | /1024
|  | 0x01 | 0x76 | 0x00 | 0x00 | Output Current Max |  |  |  | /15 | /15 if Pin 9 and Pin 10 are connected (to release 75A max current)
|  | 0x01 | 0x78 | 0x00 | 0x00 | Input Voltage |  |  |  | /1024
|  | 0x01 | 0x7F | 0x00 | 0x00 | Output Temperature |  |  |  | /1024
|  | 0x01 | 0x81 | 0x00 | 0x00 | Output Current |  |  |  | /1024 | This output current appears more accurate (on my single unit/sample)
|  | 0x01 | 0x82 | 0x00 | 0x00 | Output Current |  |  |  | /1024 | Not sure what this is?
|  | 0x01 | 0x83 | 0x00 | 0x10 | Unknown- normally zero
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | 0: ID; 4: Value | Value Multiplier
Set Data: | 0x108180FE* | 0x01 | 0x00 | 0x00 | 0x00 | On-line Output Voltage |  |  |  | V * 102 | Acceptable range 41.5 to 58.5V in 0.1V steps. Example: 460 (46.0V) * 102 = 00 00 B7 48
|  | 0x01 | 0x01 | 0x00 | 0x00 | Off-line/Default Output Voltage |  |  |  | V * 102 | Acceptable range 48 to 58.5V in 0.1V steps
|  | 0x01 | 0x02 | 0x00 | 0x00 | Overvoltage Protection? (Untested) |  |  |  | V * 102 | Acceptable range 56.5 to 60.5V (as per datasheet)
|  | 0x01 | 0x03 | 0x00 | 0x00 | On-line Current Limit |  |  |  | A * 1.5 | Acceptable range 0 to 90.5A in 0.1A steps. Example: 500 (50.0 A) * 1.38 = 00 00 02 B2 | *1.5 if in full power mode
|  | 0x01 | 0x04 | 0x00 | 0x00 | Off-line/Default Output Current Limit |  |  |  | A * 1.5 | Acceptable range 0 to 90.5A in 0.1A steps | *1.5 if in full power mode
|  | 0x01 | 0x07 | 0x00 | 0x00 | Current limit?? |  |  |  | A * 1.157 | Not tested…
|  | 0x01 | 0x32 | 0x00 | 0xXX | 0x00 | 0x00 | 0x00 | 0x00 | - | XX: 01 - disable Huawei (standby mode), 00 - enable Huawei
|  | 0x01 | 0x34 | 0x00 | 0xXX | 0x00 | 0x00 | 0x00 | 0x00 |  | XX: 01 -Turn on the fans at full power, 00 - automatic fan speed control (On-line)
|  | 0x01 | 0x35 | 0x00 | 0xXX | 0x00 | 0x00 | 0x00 | 0x00 |  | XX: 01 -Turn on the fans at full power, 00 - automatic fan speed control (Off-line)
Value Multiplier
| 0x1001117e **** | 0x00 | 0x01 | 0x00 | 0x01 | 0x00 | 0x00 | 0x00 | 0x00 |  | Byte 3 is Output Enabled Byte, It is 1 when the unit is hibernating and 0 when it is ON
|  | 0x00 | 0x01 | 0x00 | 0x00 | Output Current |  |  |  | /15 | This is an unsolicited message reporting the DC current, encoded in the last four bytes
The rectifier can operate in two states:
Off-line is when there is no CAN communication (i.e. standalone operation). This occurs on power-up or if CAN communication has timed-out (Orange LED slowly blinking).
On-line values are only valid when CAN communication is present (Orange LED not blinking). These values are volatile and reset to default on loss of CAN comms.
CAN communication time-out is approximately 60 seconds. i.e. if you stop sending valid CAN messages to the rectifier, the rectifier will switch to Off-line/Default values in approximately 60 seconds.
*0x108180FE for first Huawei, 0x108280FE for second Huawei, etc. 0x108080FE for all units in the system
** 0x108040FE to request status messages from all recitfiers, when more than one Rectifier is on the CAN BUS you can use 0x108140FE to request status from rectifier 1; 0x108240FE to request from No.2 rectifier etc
***0x1081407F is the ID that reports for the first rectifier (true also when only one is on the BUS); 0x1082407F is the ID for status messages from No.2 rectifier etc.
****0x1001117e for multible unit the message ID is following the same logic 0x1001117e 0x1002117 e0x1003117e etc…
Fan-speed control:
Request Data Frames: | 0x108182FE | 0x01 | 0x87 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | 0: ID; 4: Value | Value Multiplier
Receive Data: | 0x1081827F | 0x01 | 0x87 | auto FAN duty |  | SET min FAN duty |  | RPM |  | /256
Value Multiplier
Set Data: | 0x108080FE | 0x01 | 0x14 | Percent Duty Cycle |  | 0x00 | 0x00 | 0x00 | 0x00 | *256